## Pkg-I
Queries on Pakage-I
Sl. No. | Clause/Item No. | Description | Pre-Bid Queries | REPLY
1 | 3.1.20 | REMOVAL OF COMPONENTS | The GIS shall be designed so that any component of the GIS can be easily removed. As minimum flexibility in the layout arrangement, it shall be possible to remove the circuit breaker with both bus bar remaining in service and it shall be possible to remove the dis connector of the bus bars, with one bus bar remaining in service. | Accepted
2 | 3.2.1 | CIRCUIT BREAKER General | The GIS circuit breakers shall comply with the following general requirements for circuit breakers and the latest revisions of the relevant IEC specifications. Circuit-breakers shall be the SF6 gas insulated type of single phase or single phase insulated & three phase encapsulated design with the specified ratings. The breaker shall be Self-Blast / Puffer type principleand consist of one interrupting arcing chambers. Please note that for 132kV GIS Auto puffer principle is more reliable and necessary to fulfill new C2 duty requirement .In case of puffer principle quenching force is constant and this can lead to current chopping and restrike. | Both type Accepted
3 | 3.2.6 | CURRENT TRANSFORMERS Position of the Current Transformers and Cores, Ratios and Characteristics. | The number and position of the current transformers relative to the circuit-breakers, disconnectors and earthing switches shall be as detailed in the attached single line diagram. However, there must have possibility of provision of CT on either side of CB. Considering number of cores we are able to accommodate cores on one side on Circuit breaker therefore there is no need of any provisions of CT on either side of CB. | CT required on either side of circuit breaker
4 | In Section 3-EQC, New clause is added |  | Plant and equipment to be supplied by the bidder or its Subcontractor/Manufacturer should have been installed and in successful operation for at least two Years in India". As a result of this clause there is only one Vendor qualified for Hybrid GIS (ABB). | Tender document stands
5 |  |  | For Hybrid GIS as per clarification issued by OPTCL (Corrigendum 6, Sl no 118) Cable connectivity is required for Hybrid GIS. In order to achieve the same Surge arrestor and PT should be of GIS type. However no qualified Vendor is having such a model and they have taken this as a deviation in their offer. As per Vendor Cable will terminate in LA/PT (AIS type) and connection to Hybrid GIS module is through Gas insulated Busduct instead of cable Module. | Accepted
6 |  |  | Technical Specification of 132 kV Circuit Breaker (SF6) is not yet uploaded. (Total 4 Circuit Breakers are there) | up loaded
7 |  |  | Cable Jointing bay for Double circuit not included in the revised BOQ. (As per BOQ format proposed, Jointing Bay for Single Circuit and Double circuit was there but OPTCL included jointing bay for only single circuit .There is around 7.42 Km of Double Circuit in single Trench and around 14 Nos of Jointing bay for Double circuit is required).. | presently no provision of double circuit
8 | Section 2- Bid data Sheet (BDS)- C. Preparation of Bids ;ITB 11.2(K) | New clause : One sample piece (15 meters length) each of AAAC & XLPE Cables manufactured and to be supplied by them conforming to the guranteed technical particulars duly typed tested from the laboratories mentioned in the evaluation & qulaification criteria in section-3 Note: applicable for both bidders from Employer's country and for foreign bidders(from countries of the ADB) | As per our understanding we believe that this cause shall be applicable to the successful bidder and sample piece should be supplied from the AAAC & XLPE cable suppliers at the time of execution of the contract. As we are all aware that these items are customised items and made according to the specifications provided.It is not practically possible for us to supply one sample piece (15 meters length) each of AAAC & XLPE cables during bidding stage. In view of the request you kindly amend the above clause suitably. | tender document stands
9 | Section 3-evaluation and qualification criteria (EQC) 1.1 Technical evaluation clause-2 | new clause : for technical evaluation ,one sample piece (15 meters length) each of AAAC & XLPE cables submitted by bidder shall be type tested at CPRI of the Employer's country at the cost of the bidder.The employer's determination of a bid's responsiveness shall be based on the result of the above type test |  | tender document stands
10 | 2.4.1 General Experience | (ii) For Lot-2: Experience under contracts in the role of contractor or subcontractor, for at least last Five (05) years prior to the bid submission deadline covering following activities: 33kV or higher voltage underground Cabling with Bay in respective GRID S/S. Note: The above facility (Both for Lot-1 & Lot-2) should be in satisfactory operation for at least 01 (one) year from the date of commissioning. To substantiate this requirement the performance certificate from user is required to be furnished. | 1) As per tender, bidder for underground cables should have experience for extension bay. Since scope of bay is considerably very small portion of entire contract and since OPTCL is accepting manufacturer's authorization for HDD work, we request you to accept manufacturer's authorization for bay experience also as value of bay is very less in comparison to HDD work. | Tender document stands
11 | 2.4.2 Specific Experience: a) Contracts of Similar or higher Size and Nature | (ii) For Lot-2 : The bidder must have successfully executed XLPE underground Cable laying work at least of 50KM (Cable Length) of 110 kV or higher voltage class for any Transmission Utility during Last ten (10) Financial Years preceding to the year of NIT. Note: The above facility should be in satisfactory operation for at least 01 (one) year from the date of commissioning. To substantiate this requirement the performance certificate from user is required to be furnished. | As EHV transmission line through underground cable system has started in last 2-3 years in major utilities, OPTCL will find very less contractors who has this experience. We request you to please change the Experience clause as " must have experience of erection of 30 Kms. from which 5 Kms. is working satisfactory". | Tender document stands
12 | New clause | New Clause: Plant and equipment such as Transformers, GIS Switch Gears, Control Relay Panel , CT & PT, CVT, LA, VCB, and UG XLPE Cables to be supplied by the bidder or its Sub- Contractor/ Manufacturer should have been. Installed and in sucessful operation for at least two years in India. | This should be not applicable in 132 KV cables and accessories , because EHV cables system has started in major utilities in India from last 2-3 years. With this clause OPTCL will find very less bidders. | Tender document stands
13 |  | Submission of type test report for UG XLPE type test report of same voltage class and same or higher cable size as per the GTP shall be acceptable. | we request you to change - Type test certificate should be for 132 KV or above and for 800 sq.mm copper cable or above size | Tender document stands
14 | ITB 22.2 | i. Joint Venture/ Consortium/ Association Agreement duly signed by all parties stating that all parties shall be jointly or severally liable on non-judicial stamp paper of appropriate value as per the format prescribed in section-6. | Format of Joint Venture/ Consortium/ Association Agreement is missing in tender documents | Tender document stands
15 |  |  | We request you to provide the specification for 132kV Bus Bar since the same is not available in the standard OPTCL specification. | busbar of 2000A capacity in GIS to be designed
16 |  |  | As per price schedule Civil supply items are mentioned in Supply schedule (Schedule 1 & Schedule 2). But in Schedule 4 (Installation and other services) only Transportation and Erection, testing & commissioning of civil works was mentioned. We cannot quote Civil supply in Supply schedule. If we quote that will be treated as works contrac. Request you change the price schedule accordingly. | The Bidder has to Quote the "Materials for civil construction in Supply item"
17 |  |  | The interconnection between 33kV GIS and 33kV cable air termination kit at Gantry is not clear. How ever in Pre bid Corrigendum dt 24th Aug in Sl. No. 38 it has been mentioned that the same is not applicable. In that case how 33kV AIS LA and termination kit to be erected. | In the said queries it was asked for connecting with cable to other 33kV S/s which is "Not applicable" However the Termination Kit for 33kV included in Price Schedule
18 |  |  | As per Price Schedule Sl.No.15.2, the numbers of outdoor AIS cable termination kits are 5 (five) Nos. Then what about the quantity of indoor termination kit at GIS end and also as per Pre Bid Corrigendum dt 24th Aug Sl. No. 26, please elaborate how 250 KVA station Transformer to be connected at Gantry. | The 33 kV GIS side Indoor termination kit included in GIS system Stn Trf to be connected as shown in the SLD
19 |  |  | As per PS Sl. No. 1.9, 132kV Indoor termination kit suitable for 1Cx630 Sq.mm (GIS side for Line bay module). Here 630 Sq mm may came here by printing mistake, which is likely to be changed to 800 Sq mm. Please confirm and issue revised PS. | Price schedule stands
20 |  |  | In 33kV GIS, 3phase 3Cx95sq mm XLPE cable termination kit not considered in Price schedule for Station Transformer. Please revise the price schedule and confirm. | Station transformer is outdoor type hence no requirement of HT cable
21 |  |  | The quantity of station transformer is miss matching with SLD and Price schedule and subsequently quantity of cable termination kit for the same needs to be changed. Please confirm and issue the revised SLD /PS. | Price schedule stands
22 |  | The hybrid equipment shall be suitable for Main and Transfer busbar system | The hybrid equipment shall be suitable for single Main busbar system | Accepted